Vora Control Methods

Intern Onboarding Reference

June 2026

# Overview

All controllers share the same base interface: room temperature (T_r), room humidity (RH_r), outdoor temperature (T_out), outdoor humidity (RH_out), and simulation time (t). Occupancy-aware controllers add a binary occ input. All outputs are: fan speed command (0-3), air direction, supply temperature, desired setpoints, and temperature/humidity errors. Controllers update every 60 seconds and hold their last command between updates.

# Control Algorithms

| Function | Inputs | Logic Summary |
| --- | --- | --- |
| Adaptive MPC | t, T_r, RH_r, T_out, RH_out | Evaluates 11 discrete fan/supply-temp action pairs over a 20-minute horizon. Accumulates a cost that penalises comfort violations, preferred-zone deviation, estimated AC energy, fan speed, and command switching. Picks the lowest-cost feasible action; falls back to least-violation if none is feasible. Hard safety overrides enforce overcooling protection, temperature/humidity recovery, and fan ramp limiting. |
| Rule-based Controller | t, T_r, RH_r, T_out, RH_out | Scores 4 fan-level candidates (0-3) with a one-step comfort prediction. Supply temperature is derived from the error relative to the adaptive setpoint. Score combines comfort penalty (ASHRAE 55 bounds), tracking penalty, switching penalty, and energy cost at a fixed tariff. Applies safety overrides for overcooling, high temperature/humidity, and fan-jump limiting. |
| Universal Adaptive MPC (MPC1 v1) | t, T_r, RH_r, T_out, RH_out | Runs an online adaptive model that continuously updates heat-rate, humidity-rate, cooling-gain, and dehumidification-gain from measured room response. Searches 18 actions (20 in severe conditions) over a 30-minute horizon, minimising comfort violations, preferred-zone error, Qatar electricity cost proxy, and switching/short-cycling penalties. Comfort feasibility is prioritised over cost in selection. |
| Robust Predictive MPC (MPC1 v2) | t, T_r, RH_r, T_out, RH_out | Enhanced MPC with a fan heat-rate penalty and an improved room prediction model (predict_room_step_best). Adds a forecast helper that checks peak predicted temperature over the horizon to act pre-emptively. Shares the same adaptive structure and safety overrides as MPC1 v1, but with stronger overcooling and fan-heat awareness tuned for Qatar conditions. |
| Robust Universal Adaptive MPC (MPC1 v3 - humidity-ratio) | t, T_r, RH_r, T_out, RH_out | Upgrades MPC1 v2 by tracking absolute humidity ratio (w, kg/kg) instead of relative humidity, converting RH internally via RH_to_w(). The adaptation loop estimates passive w-rate and AC dehumidification-gain in absolute units. Uses 22 candidate actions (25 in emergencies) over a 30-minute horizon. The cost function is otherwise identical to MPC1 v2 but with slightly higher comfort weights. |
| Occupancy-Aware MPC v1 (MPC1 + occ v1) | t, T_r, RH_r, T_out, RH_out, occ | Extends the universal MPC with a binary occupancy input (occ: 1=occupied, 0=empty). After 20 minutes of confirmed vacancy, shifts to a mild empty-room setback: comfort bounds relax to 22-27 degC / 35-63% RH and the desired setpoint rises to 26.7 degC. Occupied mode restores full ASHRAE 55 bounds. Adaptive model, horizon, and safety overrides are unchanged from MPC1 v1. |
| Occupancy-Aware MPC v2 (MPC1 + occ v2) | t, T_r, RH_r, T_out, RH_out, occ | Refined version of the occupancy-aware MPC, described as built on the best-performing prior controller. Applies the same delayed empty-mode activation (20-minute hold) and identical setback envelope. Key difference is tighter integration with the higher-quality adaptive model from MPC1 v2/v3, inheriting its short-cycle penalty, on/off timers, and fan-ramp limiting logic. |

# Human Behavior Simulations

These are not optimisation controllers — they simulate realistic human AC usage patterns to serve as energy-consumption baselines for comparing against the smart controllers.

| Simulation | Inputs | Behavior Summary |
| --- | --- | --- |
| Aggressive Human Controller | t, T_r, RH_r, T_out, RH_out | Represents a user targeting a low setpoint (20 degC) with aggressive reactions: sets fan=3, Tsup=12 degC whenever room exceeds setpoint; holds fan=2, Tsup=16 degC when close to setpoint; turns off only after overcooling below it. A humidity override (RH > 60%) forces maximum cooling. No energy optimisation or predictive logic. |
| Maximum-Cooling Human Controller | t, T_r, RH_r, T_out, RH_out | Simulates a user who wants the room to always feel cold (setpoint 22 degC). Keeps cooling active even at or below setpoint, stepping down fan level only as the room becomes progressively colder. Shuts off only when room drops below 19 degC. Humidity override mirrors aggressive behavior. No comfort band or energy awareness. |

All comfort bounds follow ASHRAE 55 (23-26.5 degC, 40-60% RH) unless noted. Adaptive controllers update their room model online from measured sensor response. Qatar electricity tariff used in cost calculations: 0.115 QAR/kWh.